## Utility URP -SS file
PARAMETER | VALUE | Units | Units | Notes
COMMENT | THESE ARE THE UTILITY SPECIFIED SETTINGS
MT_FILE_INFO_TYPE | SS |  |  | Context of the data in the file - SS is the utility specified settings file -AS is the returned As Set file
COMMENT | THESE SETTING ARE APPLICABLE FOR THE FOLLOWING CONDITIONS
MT_UTILITY_NAME | PEOPLES_ENERGY_COOPERATIVE |  |  | Utility Name
MT_COUNTRY | United States of America
MT_STATE | Minnesota
MT_APPLICABILITY_DATE | 09/01/2023 |  |  | Date of applicabilty (mm/dd/yyyy format)
MT_DER_SITE_NAME | Generic_Residential |  |  | Site name - used for site specific settings
MT_DER_OWNER_NAME | Generic_Residential |  |  | DER Owner - site specific information
MT_POWER_CONVERSION_ DEV-APP | INVERTER |  | Selection | Power Conversion device type for which this setting files applies (could be Inverter - Battery Storage - other ' etc.)
MT_NP_NORMAL_OP_ CAT-APP | CAT_B |  | Multi-List | Applicable Normal Performance Category
MT_NP_ABNORMAL_OP_ CAT-APP | CAT_III |  | Mulit-List | Applicable abnormal performance category
MT_NP_P_MAX-MIN-APP | 0.0 | W | Number | applicable DER size - Active Power rating (W) - Min
MT_NP_P_MAX-MAX-APP | 1000000 | W | Number | applicable DER size - Active Power rating (W) - Max (This URP applies unless otherwise directed by utilty to use a custom URP)
MT_NP_AC_V_ NOM-APP | 120-240-208-277-480-600 | Vac | Number | String with dash- separated numbers that represent applicable nominal voltages for this settings file
MT_SERVICE_TYPE |  |  | Multi-List | Service type(s) for which this settings file is applicable (This field is not included in Minnesota Standard URP CSV -SS file)
MT_PRIMARY_POWER_ SOURCE | SOLAR-WIND-ESS |  | Multi-List | Primary power source(s) for which this settings file is applicable
MT_APPLICATION_PURPOSE |  |  | Multi-List | Application purpose(s) for which this settings file is applicable (This field is not included in Minnesota Standard URP CSV -SS file)
MT_PRIMARY_MOVER | PHOTOVOLTAIC_PANELS-NONE |  | Multi-List | Primary mover type(s) for which this settings file is applicable
MT_VARIABLE_GENERATION_TYPE | VARIABLE-NON_VARIABLE |  | Multi-List | Variable generation type
COMMENT | ENTER_ SERVICE_PARAMETERS (1547 Defaults)
ES_PERMIT_SERVICE-SS | ENABLED |  | Selection List | Permit service function enable. This function is activated by request from the Area EPS Operator
ES_V_LOW-SS | 0.917 | V p.u. | Number | Enter service voltage - low - setting. Per unit value based on NP_AC_V_NOM (voltage base)
ES_V_HIGH-SS | 1.05 | V p.u. | Number | Enter service voltage - high - setting. Per unit value based on NP_AC_V_NOM (voltage base)
ES_F_LOW-SS | 59.5 | Hz | Number | Frequency in Hz, and shall be reported to 3 decimal places
ES_F_HIGH-SS | 60.1 | Hz | Number | Frequency in Hz, and shall be reported to 3 decimal places.
ES_DELAY-SS | 300 | Seconds | Number | Minimum intentional enter service delay (1547 allowed range is 0-600 seconds)
ES_RANDOMIZED_DELAY-SS | 0 | Seconds | Number | Enter service randomized delay (optional feature in IEEE Std 1547-2018) (1547 allowed range is 0-600 seconds)
ES_RAMP_RATE-SS | 300 | Seconds | Number | Enter service soft-start duration in seconds. Time from zero to 100% of NP_P_MAX. (1547 allowed range is 1-1000 seconds)
COMMENT | CONSTANT_POWER_FACTOR_MODE_ PARAMETERS
CONST_PF_MODE_ENABLE-SS | DISABLED |  | Selection List | Constant power factor mode enable
CONST_PF_EXCITATION-SS | ABS |  | Selection List | Under or over excited (Absorbing slected)
CONST_PF-SS | 0.98 | PF | Number | Constant power factor setting, no sign should be used
CONST_Q_MODE_ENABLE-SS | DISABLED |  | Selection List | Constant reactive power mode select
CONST_Q-SS | 0 | Var p.u | Number | Injecting reactive power setting. Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
COMMENT | VOLT-VAR_MODE_PARAMETERS (1547 STANDARD VALUES)
QV_MODE_ENABLE-SS | ENABLED |  | Selection List | Voltage-Reactive power mode enable.
QV_VREF-SS | 1.0 | V p.u. | Number | Per unit value based on NP_AC_V_NOM (voltage base)
QV_VREF_AUTO_MODE-SS | DISABLED |  | Selection List | Autonomous Vref adjustment enable.
QV_VREF_TIME-SS | 5 | Seconds | Number | Vref adjustment time constant in seconds as specified by the area EPS operator
QV_CURVE_V1-SS | 0.92 | V p.u. | Number | Volt-VAr point V1 setting. Per unit value based on NP_AC_V_NOM.
QV_CURVE_Q1-SS | 0.44 | Var p.u | Number | VArs at V1 setting. Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QV_CURVE_V2-SS | 0.98 | V p.u. | Number | Volt-VAr point V2 setting. Per unit value based on NP_AC_V_NOM.
QV_CURVE_Q2-SS | 0.0 | Var p.u | Number | VArs at V2 setting. Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QV_CURVE_V3-SS | 1.02 | V p.u. | Number | Volt-VAr point V3 setting. Per unit value based on NP_AC_V_NOM.
QV_CURVE_Q3-SS | 0.0 | Var p.u | Number | VArs at V3 setting. Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QV_CURVE_V4-SS | 1.08 | V p.u. | Number | Volt-VAr point V4 setting. Per unit value based on NP_AC_V_NOM.
QV_CURVE_Q4-SS | -0.44 | Var p.u | Number | VArs at V4 setting. Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QV_OLRT-SS | 5 | Seconds | Number | Volt-VAr open-loop response time
COMMENT | WATT-VAR_CONTROL_PARAMETERS
QP_MODE_ENABLE-SS | DISABLED |  | Selection List | Active power-Reactive power mode enable (with Watt-Var Mode disabled the rest of these settings are blank)
QP_CURVE_P3_GEN-SS |  | P p.u | Number | Watt-VAr point P3 setting (generating active power). Per unit value based on NP_P_MAX.
QP_CURVE_P2_GEN-SS |  | P p.u | Number | Watt-VAr point P2 setting (generating active power). Per unit value based on NP_P_MAX.
QP_CURVE_P1_GEN-SS |  | P p.u | Number | Watt-VAr point P1 setting (generating active power). Per unit value based on NP_P_MAX.
QP_CURVE_P1_LOAD-SS |  | P p.u | Number | Watt-VAr point P1 setting (absorbing active power). Per unit value based on NP_P_MAX_CHARGE.
QP_CURVE_P2_LOAD-SS |  | P p.u | Number | Watt-VAr point P2 setting (absorbing active power). Per unit value based on NP_P_MAX_CHARGE.
QP_CURVE_P3_LOAD-SS |  | P p.u | Number | Watt-VAr point P3 setting (absorbing active power). Per unit value based on NP_P_MAX_CHARGE.
QP_CURVE_Q3_GEN-SS |  | Var p.u | Number | VArs at point P3 setting (generating active power). Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QP_CURVE_Q2_GEN-SS |  | Var p.u | Number | VArs at point P2 setting (generating active power). Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QP_CURVE_Q1_GEN-SS |  | Var p.u | Number | VArs at point P1 setting (generating active power). Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QP_CURVE_Q1_LOAD-SS |  | Var p.u | Number | VArs at point P1 setting (absorbing active power). Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QP_CURVE_Q2_LOAD-SS |  | Var p.u | Number | VArs at point P2 setting (absorbing active power). Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QP_CURVE_Q3_LOAD-SS |  | Var p.u | Number | VArs at point P3 setting (absorbing active power). Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
COMMENT | VOLT-WATT_CONTROL_PARAMETERS (1547 STANDARD VALUES)
PV_MODE_ENABLE-SS | ENABLED |  | Selection List | Voltage-Active power mode enable
PV_CURVE_V1-SS | 1.06 | V p.u. | Number | Volt-Watt point V1 setting. Per unit value based on NP_AC_V_NOM.
PV_CURVE_P1-SS | 1.0 | P p.u. | Number | Watts at point V1 setting. Per unit value based on NP_P_MAX.
PV_CURVE_V2-SS | 1.10 | V p.u. | Number | Volt-Watt point V2 setting. Per unit value based on NP_AC_V_NOM.
PV_CURVE_P2-SS | 0.0 | P p.u. | Number | Watts at point V2 setting. Per unit value based on NP_P_MAX or NP_P_MAX_CHARGE. Negative values indicate active power absorption.
PV_OLRT-SS | 10 | Seconds | Number | Volt-Watt - Open loop response time
COMMENT | OVER_UNDER_VOLTAGE_MUST_TRIP_PARAMETERS (MISO RECOMMENDED VALUES)
OV2_TRIP_V-SS | 1.20 | V p.u. | Number | OV2 must trip over-voltage setting. Per unit value based on NP_AC_V_NOM.
OV2_TRIP_T-SS | 0.16 | Seconds | Number | OV2 must trip duration setting
OV1_TRIP_V-SS | 1.10 | V p.u. | Number | OV1 must trip over-voltage setting. Per unit value based on NP_AC_V_NOM.
OV1_TRIP_T-SS | 2.0 | Seconds | Number | OV1 must trip duration setting
UV1_TRIP_V-SS | 0.70 | V p.u. | Number | UV1 must trip under-voltage setting. Per unit value based on NP_AC_V_NOM.
UV1_TRIP_T-SS | 5.0 | Seconds | Number | UV1 must trip duration setting
UV2_TRIP_V-SS | 0.45 | V p.u. | Number | UV2 must trip under-voltage setting. Per unit value based on NP_AC_V_NOM.
UV2_TRIP_T-SS | 0.32 | Seconds | Number | UV2 must trip duration setting
COMMENT | OVER_UNDER_FREQUENCY_MUST_TRIP_PARAMETERS (MISO RECOMENDED VALUES)
OF2_TRIP_F-SS | 62.0 | Hz | Number | OF2 must trip over-frequency magnitude setting. Frequency values shall be reported to 3 decimal places.
OF2_TRIP_T-SS | 0.16 | Seconds | Number | OF2 must trip duration setting
OF1_TRIP_F-SS | 61.2 | Hz | Number | OF1 must trip over-frequency magnitude setting. Frequency values shall be reported to 3 decimal places.
OF1_TRIP_T-SS | 300.0 | Seconds | Number | OF1 must trip duration setting
UF1_TRIP_F-SS | 58.5 | Hz | Number | UF1 must trip under-frequency magnitude setting. Frequency values shall be reported to 3 decimal places.
UF1_TRIP_T-SS | 300.0 | Seconds | Number | UF1 must trip duration setting
UF2_TRIP_F-SS | 56.5 | Hz | Number | UF2 must trip under-frequency magnitude setting. Frequency values shall be reported to 3 decimal places.
UF2_TRIP_T-SS | 0.16 | Seconds | Number | UF2 must trip duration setting
PF_DBOF-SS | 0.036 | Hz | Number | Over frequency deadband offset from nominal frequency in Hz. Frequency values shall be reported to 3 decimal places.
PF_DBUF-SS | 0.036 | Hz | Number | Under frequency deadband offset from nominal frequency in Hz. Frequency values shall be reported to 3 decimal places.
PF_KOF-SS | 0.05 | Number | Number | Over frequency per unit frequency change corresponding to a 1 per unit power change (frequency droop).
PF_KUF-SS | 0.05 | Number | Number | Under frequency per unit frequency change corresponding to a 1 per unit power change (frequency droop).
PF_OLRT-SS | 5.0 | Seconds | Number | Frequency-Active power open-loop response time

## Installer -AS File
PARAMETER | VALUE | Units | Required Field | Units | Notes
COMMENT | THIS FILE IS THE AS-SET OR -AS FILE FOR THE INSTALLATION
MT_FILE_INFO_TYPE | AS |  |  |  | Context of the data in the file - SS is the utility specified settings file -AS is the returned As Set file
COMMENT | BASIC_INVERTER_INFORMATION
NP_P_MAX |  | W | Required | Number | Active power rating in watts at unity power factor
NP_P_MAX_OVER_PF |  | W |  | Number | Active power rating in watts at specified over-excited power factor
NP_OVER_PF |  |  |  | Number | Over-excited power factor (VArs injected)
NP_P_MAX_UNDER_PF |  | W |  | Number | Active power rating in watts at specified under-excited power factor
NP_UNDER_PF |  |  |  | Number | Under-excited power factor (VArs absorbed)
NP_VA_MAX |  | VA | Required | Number | Maximum apparent power rating in volt-amperes
NP_NORMAL_OP_CAT | CAT_A |  | Required | Selection List | Normal operating performance category
NP_ABNORMAL_OP_CAT | CAT_III |  | Required | Selection List | Abnormal operating performance category
NP_Q_MAX_INJ |  |  |  | Number | Maximum injected reactive power rating in volt-amperes reactive
NP_Q_MAX_ABS |  |  |  | Number | Maximum absorbed reactive power rating in volt-amperes reactive
NP_P_MAX_CHARGE |  |  |  | Number | Maximum active power charge rating in watts
NP_APPARENT_POWER_ CHARGE_MAX |  |  |  | Number | Maximum apparent power charge rating in volt-amperes. May differ from the apparent power maximum rating
NP_AC_V_NOM-SS |  |  | Required | Number | Base nominal AC voltage rating in RMS Vac
NP_AC_V_MAX |  |  |  | Number | Maximum output RMS AC voltage (VH) in the continuous operating region
NP_AC_V_MIN |  |  |  | Number | Minimum output RMS AC voltage (VL) in the continuous operating region
NP_SUPPORTED_MODES | QV-QP-PV-CONST_PF-CONST_Q-PF |  | Required | Mulit-List | Indication of support for each control mode function separated by dashes
NP_REACTIVE_SUSCEPTANCE |  |  |  | Number | Reactive susceptance that remains connected to the Area EPS in the cease to energize and trip state
NP_MANUFACTURER |  |  | Required | Text | Manufacturer
NP_MODEL |  |  | Required | Text | Model
NP_SERIAL_NUM |  |  | Required | Text | Serial number
NP_FW_VER |  |  | Required | Text | Firmware version
AP_LIMIT_ ENABLE |  |  | Required | P p.u | Limit active power function ENABLED or DISABLED
AP_LIMIT |  |  | Required | Number | Active power limit setting. Per unit value based on NP_P_MAX or NP_P_MAX_CHARGE. Negative values indicate active power absorption
COMMENT | ENTER_ SERVICE_PARAMETERS (1547 Defaults)
ES_PERMIT_SERVICE-AS | ENABLED |  | Required | Selection List | Permit service function enable. This function is activated by request from the Area EPS Operator
ES_V_LOW-AS | 0.917 | V p.u. | Required | Number | Enter service voltage - low - setting. Per unit value based on NP_AC_V_NOM (voltage base)
ES_V_HIGH-AS | 1.05 | V p.u. | Required | Number | Enter service voltage - high - setting. Per unit value based on NP_AC_V_NOM (voltage base)
ES_F_LOW-AS | 59.5 | Hz | Required | Number | Frequency in Hz, and shall be reported to 3 decimal places
ES_F_HIGH-AS | 60.1 | Hz | Required | Number | Frequency in Hz, and shall be reported to 3 decimal places.
ES_DELAY-AS | 300.0 | Seconds | Required | Number | Minimum intentional enter service delay
ES_RANDOMIZED_DELAY-AS | 0 | Seconds | Required | Number | Enter service randomized delay (optional feature in IEEE Std 1547-2018)
ES_RAMP_RATE-AS | 300.0 | Seconds | Required | Number | Enter service soft-start duration in seconds. Time from zero to 100% of NP_P_MAX.
COMMENT | CONSTANT_POWER_FACTOR_MODE_ PARAMETERS
CONST_PF_MODE_ENABLE-AS | DISABLED |  | Required | Selection List | Constant power factor mode enable
CONST_PF_EXCITATION-AS |  |  |  | Selection List | Under or over excited
CONST_PF-AS | 0.98 | PF |  | Number | Constant power factor setting, no sign should be used
CONST_Q_MODE_ENABLE-AS | DISABLED |  |  | Selection List | Constant reactive power mode select
CONST_Q-AS |  | Var p.u |  | Number | Injecting reactive power setting. Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
COMMENT | VOLT-VAR_MODE_PARAMETERS (1547 STANDARD VALUES)
QV_MODE_ENABLE-AS | ENABLED |  | Required | Selection List | Voltage-Reactive power mode enable.
QV_VREF-AS | 1.0 | V p.u. | Required | Number | Per unit value based on NP_AC_V_NOM (voltage base)
QV_VREF_AUTO_MODE-AS | DISABLED |  | Required | Selection List | Autonomous Vref adjustment enable.
QV_VREF_TIME-AS | 5.0 | Seconds | Required | Number | Vref adjustment time constant in seconds as specified by the area EPS operator
QV_CURVE_V1-AS | 0.92 | V p.u. | Required | Number | Volt-VAr point V1 setting. Per unit value based on NP_AC_V_NOM.
QV_CURVE_Q1-AS | 0.44 | Var p.u | Required | Number | VArs at V1 setting. Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QV_CURVE_V2-AS | 0.98 | V p.u. | Required | Number | Volt-VAr point V2 setting. Per unit value based on NP_AC_V_NOM.
QV_CURVE_Q2-AS | 0.0 | Var p.u | Required | Number | VArs at V2 setting. Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QV_CURVE_V3-AS | 1.02 | V p.u. | Required | Number | Volt-VAr point V3 setting. Per unit value based on NP_AC_V_NOM.
QV_CURVE_Q3-AS | 0.0 | Var p.u | Required | Number | VArs at V3 setting. Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QV_CURVE_V4-AS | 1.08 | V p.u. | Required | Number | Volt-VAr point V4 setting. Per unit value based on NP_AC_V_NOM.
QV_CURVE_Q4-AS | -0.44 | Var p.u | Required | Number | VArs at V4 setting. Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QV_OLRT-AS | 5.0 | Seconds | Required | Number | Volt-VAr open-loop response time
COMMENT | WATT-VAR_CONTROL_PARAMETERS
QP_MODE_ENABLE-AS | DISABLED |  | Required | Selection List | Active power-Reactive power mode enable
QP_CURVE_P3_GEN-AS |  | P p.u |  | Number | Watt-VAr point P3 setting (generating active power). Per unit value based on NP_P_MAX.
QP_CURVE_P2_GEN-AS |  | P p.u |  | Number | Watt-VAr point P2 setting (generating active power). Per unit value based on NP_P_MAX.
QP_CURVE_P1_GEN-AS |  | P p.u |  | Number | Watt-VAr point P1 setting (generating active power). Per unit value based on NP_P_MAX.
QP_CURVE_P1_LOAD-AS |  | P p.u |  | Number | Watt-VAr point P1 setting (absorbing active power). Per unit value based on NP_P_MAX_CHARGE.
QP_CURVE_P2_LOAD-AS |  | P p.u |  | Number | Watt-VAr point P2 setting (absorbing active power). Per unit value based on NP_P_MAX_CHARGE.
QP_CURVE_P3_LOAD-AS |  | P p.u |  | Number | Watt-VAr point P3 setting (absorbing active power). Per unit value based on NP_P_MAX_CHARGE.
QP_CURVE_Q3_GEN-AS |  | Var p.u |  | Number | VArs at point P3 setting (generating active power). Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QP_CURVE_Q2_GEN-AS |  | Var p.u |  | Number | VArs at point P2 setting (generating active power). Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QP_CURVE_Q1_GEN-AS |  | Var p.u |  | Number | VArs at point P1 setting (generating active power). Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QP_CURVE_Q1_LOAD-AS |  | Var p.u |  | Number | VArs at point P1 setting (absorbing active power). Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QP_CURVE_Q2_LOAD-AS |  | Var p.u |  | Number | VArs at point P2 setting (absorbing active power). Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
QP_CURVE_Q3_LOAD-AS |  | Var p.u |  | Number | VArs at point P3 setting (absorbing active power). Per unit value based on NP_VA_MAX. Negative signs shall be used to indicate absorbing VAr.
COMMENT | VOLT-WATT_CONTROL_PARAMETERS (1547 STANDARD VALUES)
PV_MODE_ENABLE-AS | ENABLED |  | Required | Selection List | Voltage-Active power mode enable
PV_CURVE_V1-AS | 1.06 | V p.u. | Required | Number | Volt-Watt point V1 setting. Per unit value based on NP_AC_V_NOM.
PV_CURVE_P1-AS | 1 | V p.u. | Required | Number | Watts at point V1 setting. Per unit value based on NP_P_MAX.
PV_CURVE_V2-AS | 1.10 | V p.u. | Required | Number | Volt-Watt point V2 setting. Per unit value based on NP_AC_V_NOM.
PV_CURVE_P2-AS | 0.0 | V p.u. | Required | Number | Watts at point V2 setting. Per unit value based on NP_P_MAX or NP_P_MAX_CHARGE. Negative values indicate active power absorption.
PV_OLRT-AS | 10.0 | V p.u. | Required | Number | Volt-Watt - Open loop response time
COMMENT | OVER_UNDER_VOLTAGE_MUST_TRIP_PARAMETERS (MISO RECOMMENDED VALUES)
OV2_TRIP_V-AS | 1.20 | V p.u. | Required | Number | OV2 must trip over-voltage setting. Per unit value based on NP_AC_V_NOM.
OV2_TRIP_T-AS | .16 | Seconds | Required | Number | OV2 must trip duration setting
OV1_TRIP_V-AS | 1.10 | V p.u. | Required | Number | OV1 must trip over-voltage setting. Per unit value based on NP_AC_V_NOM.
OV1_TRIP_T-AS | 2 | Seconds | Required | Number | OV1 must trip duration setting
UV1_TRIP_V-AS | 0.70 | V p.u. | Required | Number | UV1 must trip under-voltage setting. Per unit value based on NP_AC_V_NOM.
UV1_TRIP_T-AS | 5 | Seconds | Required | Number | UV1 must trip duration setting
UV2_TRIP_V-AS | 0.45 | V p.u. | Required | Number | UV2 must trip under-voltage setting. Per unit value based on NP_AC_V_NOM.
UV2_TRIP_T-AS | .32 | Seconds | Required | Number | UV2 must trip duration setting
COMMENT | OVER_UNDER_FREQUENCY_MUST_TRIP_PARAMETERS (MISO RECOMENDED VALUES)
OF2_TRIP_F-AS | 62.0 | Hz | Required | Number | OF2 must trip over-frequency magnitude setting. Frequency values shall be reported to 3 decimal places.
OF2_TRIP_T-AS | 0.16 | Seconds | Required | Number | OF2 must trip duration setting
OF1_TRIP_F-AS | 61.2 | Hz | Required | Number | OF1 must trip over-frequency magnitude setting. Frequency values shall be reported to 3 decimal places.
OF1_TRIP_T-AS | 300.0 | Seconds | Required | Number | OF1 must trip duration setting
UF1_TRIP_F-AS | 58.5 | Hz | Required | Number | UF1 must trip under-frequency magnitude setting. Frequency values shall be reported to 3 decimal places.
UF1_TRIP_T-AS | 300.0 | Seconds | Required | Number | UF1 must trip duration setting
UF2_TRIP_F-AS | 56.5 | Hz | Required | Number | UF2 must trip under-frequency magnitude setting. Frequency values shall be reported to 3 decimal places.
UF2_TRIP_T-AS | 0.16 | Seconds | Required | Number | UF2 must trip duration setting
PF_DBOF-AS | 0.036 | Hz | Required | Number | Over frequency deadband offset from nominal frequency in Hz. Frequency values shall be reported to 3 decimal places.
PF_DBUF-AS | 0.036 | Hz | Required | Number | Under frequency deadband offset from nominal frequency in Hz. Frequency values shall be reported to 3 decimal places.
PF_KOF-AS | 0.05 | Number | Required | Number | Over frequency per unit frequency change corresponding to a 1 per unit power change (frequency droop).
PF_KUF-AS | 0.05 | Number | Required | Number | Under frequency per unit frequency change corresponding to a 1 per unit power change (frequency droop).
PF_OLRT-AS | 5.0 | Seconds | Required | Number | Frequency-Active power open-loop response time